section 16410

commercial metering equipment

general

Scope

The Contractor shall furnish and install, where indicated, a free-standing, dead-front type, low voltage commercial metering switchboard, utilizing group mounted meters and circuit protective devices as specified herein, and as shown on the contract drawings.

References

The low voltage commercial metering switchboards and all components shall be designed, manufactured and tested in accordance with the latest applicable following standards:

UL Standard 891

Submittals – for Review/approval

The following information shall be submitted to the Engineer:

Front view elevation

Floor plan

Top view

Single line

Schematic diagram

Component list

Conduit entry/exit locations

Assembly ratings including:

Short-circuit rating

Voltage

Continuous current

Major component ratings including:

Voltage

Continuous current

Interrupting ratings

Cable terminal sizes

Product data sheets

Where applicable, the following additional information shall be submitted to the Engineer:

Bus connection

Connection details between close-coupled assemblies

Composite floor plan of close-coupled assemblies

Submittals – for construction

The following information shall be submitted for record purposes:

Final as-built drawings and information for items lshall incorporate all changes made during the manufacturing process

Wiring diagrams

Installation information

Qualifications

The manufacturer of this equipment shall be a manufacturer that has produced similar electrical equipment for a minimum period of five (5) years. When requested by the engineer, an acceptable list of installations with similar equipment shall be provided demonstrating compliance with this requirement.

Regulatory Requirements

The low-voltage switchboard shall be UL 891 labeled.

Delivery, Storage and Handling

Equipment shall be handled and stored in accordance with manufacturer’s instructions. One (1) copy of these instructions shall be included with the equipment at time of shipment.

Operation and Maintenance Manuals

Equipment operation and maintenance manuals shall be provided with each assembly shipped and shall include instruction leaflets, instruction bulletins and renewal parts lists where applicable, for the complete assembly and each major component.

Products

  - manufacturers

AMP – American Midwest Power Type FMU-R

Square D

General Electric

The listing of specific manufacturers above does not imply acceptance of their products that do not meet the specified ratings, features and functions. Manufacturers listed above are not relieved from meeting these specifications in their entirety. Products in compliance with the specification and manufactured by others not named will be considered only if pre-approved by the Engineer ten (10) days prior to bid date.

Ratings

The assembly shall be rated to withstand mechanical forces exerted during short-circuit conditions when connected directly to a power source having available fault current 85,000 amperes symmetrical at rated voltage.

480Y/277 or 208Y/120 Voltage rating as indicated on the drawings.

Main amperage ratings as indicated on drawings.

Construction

Switchboards shall consist of the required number of vertical sections bolted together to form a rigid assembly. Each sections structure to be constructed of die formed vertical posts and base members made from galvanized 12 gauge steel that form rigid self supporting structures to support the bussing and over current devices. The sides and rear shall be covered with removable bolt-on 14 gauge covers. All edges of all covers or hinged front panels shall be pan formed. Provide adequate ventilation within the enclosure.

All covers shall be designed with interlocking overlapping covers to inhibit water from entering the enclosure.

All sections of the switchboard shall be rear aligned with depth as shown on the drawings. All protective devices shall be group mounted. Devices shall be front removable and load connections front accessible.

The commercial metering switchboard shall be equal to AMP “Type FMU-R” switchboard utilizing the components herein specified and as shown on the drawings.

Bus

All bus bars shall be tin-plated aluminum or copper. Main horizontal bus bars shall be mounted with all three phases arranged in the same vertical or horizontal plane. Bus sizing shall be based on NEMA standard temperature rise criteria of 65 degrees C over a 40 degrees C ambient (outside the enclosure).

Provide a full capacity neutral bus where a neutral bus is indicated on the drawings.

All busses to be supported by high strength glass reinforced polyester insulating supports.

A ground bus (minimum 1/4 x 2 inch) shall be furnished firmly secured to each vertical section structure and shall extend the entire length of the switchboard.

All hardware used on conductors shall be high-tensile strength and zinc-plated. All cross bus joints shall be provided with pressed in captive threaded hardware to enable one handed tightening of cross bus connections.

Wiring/Terminations

Mechanical-type terminals shall be provided for incoming terminations and be suitable for copper or aluminum cable rated for 75 degrees C and shall be dual rated to accept (1)#6-750MCM or (2)#6-300MCM per lug

Main Protective Devices

All main devices shall be fused.  Mains above 1200A shall be fused bolted pressure switch.

Utility Meter sockets – direct read

All utility meter sockets shall be rated as indicated either 200A or 320A three phase, 7 terminal, lever bypass, ringless style.  Meter sockets should be either hot sequence or cold sequence as required by the utility.  There shall not be a door over the meters

Hot Sequence Meter Sockets

Minimum of 8 meter sockets per section

Cold Sequence Meter Sockets

Minimum of 6 meter sockets per section

All meter sockets, both 200A and 320A, either hot or cold sequence shall be twin mounted along with their corresponding disconnects in modular buckets for field installation and removal to accommodate future tenant needs.

Meter sockets shall be located in the switchboard such that the center of the utility provided meter when installed shall not be higher or lower than that specified by the utility.

Utility CT metering provisions

All utility C.T. metering provisions shall be hot sequence, adequately barriered, with a hinged door, stainless steel hinge and lockable handle, and overall dimensions and phase to phase clearance as specified by the utility.

All CT provisions 800A and less shall be modular construction for field installation and removal to accommodate future tenant needs.

CT provisions 800A and less shall accept miniature bar type CT’s.  CT provisions 1200A and greater shall except either window CT’s or bar type.

Utility CT provisions shall have the ability to either have one fully sized load side disconnect or multiple branch disconnects as indicated.

Utility CT provisions shall be located in the switchboard such that the center of the utility provided CT when installed shall not be higher or lower than that specified by the utility.

Feeder Protective devices

Fused switches 600A and less to accept class R, T or J current limiting fuses, switches 800A and greater to accept class L fuses.

Meter Socket Branch Devices

Shall be either fused switch or circuit breaker

Shall be adjacent to its corresponding meter socket, and not grouped at the bottom or top of the switchboard.

Each meter socket disconnect to have a hinged cover with locking hasp for NEMA 3R applications.

Enclosures

NEMA 3R Enclosure – Outdoor with no overall door over meters.

Nameplates

Furnish master nameplate giving switchboard designation, voltage ampere rating, short-circuit rating, manufacturer’s name, shop order number, and item number.

Finish

All exterior and non galvanized interior steel surfaces of the switchboard shall be properly cleaned and provided with an oven baked polyester powder coating paint applied electro-statically. Color and finish of the switchboard shall be ANSI 61 light gray.

- execution

  - Installation

    - The Contractors shall install all equipment per the manufacturer’s instructions, contract drawings and National Electrical Code.

    - The assembly shall be provided with adequate lifting means and shall be capable of being moved into installation position and bolted directly to the floor without the use of floor sills provided the floor is level to 1/8 inch per 3-foot distance in any direction. All necessary hardware to secure the assembly in place shall be provided by the Contractor.

  - field adjustments

    - The Contractor shall perform field adjustments of the protective devices as required to place the equipment in final operating condition.

    - Necessary field settings of devices, adjustments and minor modifications shall be carried out by the Contractor.