section 16420

Residential Mult-metering equipment

general

Scope

The Contractor shall furnish and install, where indicated, surface mount, dead-front type, low voltage residential multi-metering line-up, utilizing group mounted meters and circuit protective devices as specified herein, and as shown on the contract drawings.

References

The low voltage residential meter center and all components shall be designed, manufactured and tested in accordance with the latest applicable following standards:

UL Standard 891

Submittals – for Review/approval

The following information shall be submitted to the Engineer:

Front view elevation

Floor plan

Top view

Single line

Schematic diagram

Component list

Conduit entry/exit locations

Assembly ratings including:

Short-circuit rating

Voltage

Continuous current

Major component ratings including:

Voltage

Continuous current

Interrupting ratings

Cable terminal sizes

Product data sheets

Where applicable, the following additional information shall be submitted to the Engineer:

Bus connection

Connection details between close-coupled assemblies

Composite floor plan of close-coupled assemblies

Submittals – for construction

The following information shall be submitted for record purposes:

Final as-built drawings and information for items shall incorporate all changes made during the manufacturing process

Wiring diagrams

Installation information

Qualifications

The manufacturer of this equipment shall be a manufacturer that has produced similar electrical equipment for a minimum period of five (5) years. When requested by the engineer, an acceptable list of installations with similar equipment shall be provided demonstrating compliance with this requirement.

Regulatory Requirements

The low-voltage switchboard shall be UL 891 labeled.

Delivery, Storage and Handling

Equipment shall be handled and stored in accordance with manufacturer’s instructions. One (1) copy of these instructions shall be included with the equipment at time of shipment.

Operation and Maintenance Manuals

Equipment operation and maintenance manuals shall be provided with each assembly shipped and shall include instruction leaflets, instruction bulletins and renewal parts lists where applicable, for the complete assembly and each major component.

Products

  - manufacturers

AMP – American Midwest Power Type RM (Indoor) / RMR or FMU-R (Outdoor)

States Electric Manufacturing

General Electric

The listing of specific manufacturers above does not imply acceptance of their products that do not meet the specified ratings, features and functions. Manufacturers listed above are not relieved from meeting these specifications in their entirety. Products in compliance with the specification and manufactured by others not named will be considered only if pre-approved by the Engineer ten (10) days prior to bid date.

Ratings

The assembly shall be rated to withstand mechanical forces exerted during short-circuit conditions when connected directly to a power source having available fault current 85,000 amperes symmetrical at rated voltage.

208Y/120 Voltage rating as indicated on the drawings.

Main amperage ratings as indicated on drawings.

Construction

Meter center shall consist of the required number of vertical sections bolted together to form a continuous assembly. Each sections box to be constructed of die formed galvanized 14 gauge steel that form rigid self supporting structures to support the bussing and over current devices. The meter center front and side gutters shall be covered with removable bolt-on 14 gauge covers. All edges of all covers or hinged front panels shall be pan formed. Provide adequate ventilation within the enclosure.

All covers shall be designed with interlocking overlapping covers to inhibit water from entering the enclosure.

All sections of the switchboard shall be rear aligned with depth as shown on the drawings. All protective devices shall be group mounted. Devices shall be front removable and load connections front accessible.

The residential meter center shall be equal to AMP “Type RM” or equal for indoor or AMP “Type RMR or FMU-R” or equal for outdoor, utilizing the components herein specified and as shown on the drawings.

Bus

All bus bars shall be tin-plated aluminum or copper. Main horizontal bus bars shall be mounted with all three phases arranged in the same vertical. Bus sizing shall be based on NEMA standard temperature rise criteria of 65 degrees C over a 40 degrees C ambient (outside the enclosure).

Provide a full capacity neutral bus where a neutral bus is indicated on the drawings.

All busses to be supported by high strength glass reinforced polyester insulating supports.

All hardware used on conductors shall be high-tensile strength and zinc-plated. All cross bus joints shall be provided with pressed in captive threaded hardware to enable one handed tightening of cross bus connections.

Wiring/Terminations

Mechanical-type terminals shall be provided for incoming terminations and be suitable for copper or aluminum cable rated for 75 degrees C and shall be dual rated to accept (1)#6-750MCM or (2)#6-300MCM per lug

Main Protective Devices

All main devices shall be fused.  Mains above 1200A shall be fused bolted pressure switch.

Utility Meter sockets – direct read

All utility meter sockets shall be rated 150A single phase, 5 terminal, lever bypass, ringless style.  A minimum of 12 meters shall be able to fit into each section that is 30” wide x 10” deep x 90” high.

All meter sockets shall be twin mounted.

Meter sockets shall be located in the meter center such that the center of the utility provided meter when installed shall not be higher or lower than that specified by the utility.

Branch Feeder Protective devices

Meter Socket Branch Devices

Shall be a plug on circuit breaker rated up to 125A

Enclosures

NEMA 1 Enclosure – Indoor.

NEMA 3R Enclosure - Outdoor

Nameplates

Furnish master nameplate giving switchboard designation, voltage ampere rating, short-circuit rating, manufacturer’s name, shop order number, and item number.

Finish

All front covers shall be properly cleaned and provided with an oven baked polyester powder coating paint applied electro-statically. Color and finish of the switchboard shall be ANSI 61 light gray.

- execution

  - Installation

    - The Contractors shall install all equipment per the manufacturer’s instructions, contract drawings and National Electrical Code.

    - Install location per utility company standards.  Prior to construction, electrical contractor shall receive prior utility approval for indoor installations.

    - Indoor installations shall have common keyless entry access to meters.

    - The assembly shall be provided with adequate lifting means and shall be capable of being moved into installation position and bolted directly to the floor without the use of floor sills provided the floor is level to 1/8 inch per 3-foot distance in any direction. All necessary hardware to secure the assembly in place shall be provided by the Contractor.

  - field adjustments

    - The Contractor shall perform field adjustments of the protective devices as required to place the equipment in final operating condition.

    - Necessary field settings of devices, adjustments and minor modifications shall be carried out by the Contractor.